## Sheet1
Elevator Inventory
Building |  | Elevator Machine room | Elevator | Elevator Type | Capacity | Elevator Class | State number | Floors Served | function 1 | function 2 | function 3 | function 4 | Cladding | Doors | Elevator Equipement - Power Type | Selector Switch (Y/N) | Elevator Equipement - Panel | Elevator Equipement - Panel Location | Elevator Equipment - ATS | ATS Capacity | ATS Location | Emergency Signal (Y/N) | *Pretransfer (Y/N) | ATS Manufacturer | Cab Lighting - Normal or Emergency | Preferred Contractor | HVAC - Power Type | HVAC - Panel | HVAC - Power Location | Video | Access Control 1 | Access Control 2 | Access control 1 - Location | Access control 2 - Location | Comments - March 2024 | Comments - May 22, 2024 | Scope - All
Allied Health | Up to Contractor and material | ELM 038 / 121 | 11 | Hydraulic | 3500 | Passenger | ST 1936 | 1-5 |  |  |  |  | Paint | Paint | Emergency | N | EDP | RM 501 | (1) for building | 600a | Mech Space - 5th floor | Y | N/A | Russ Electric | [5 empty] | N |  |  |  |  | Need to understand why they do not run simultaniously. They are on (2) different breakers. | Scope seems to replace in kind, agreed? Confirm w/ Tim power requireemtns. Number 2 - car has issue with Disconnect, Brians team to test it. | Scope to Provide contacts and wiring for transfer and Pretransfer (complete System)
Allied Health | Up to Contractor and material | ELM 038 / 121 | 12 | Hydraulic | 3500 | Passenger | ST 1937 | 1-5 |  |  |  |  | Paint | Paint | Emergency | N | EDP | RM 501 | (1) for building | 600a | Mech Space - 5th floor | Y | N/A | [6 empty] | N
General Research Building | Up to Contractor and material | N/A - Basement | 2 | Traction - Basement | 3000 | Passenger | ST 1365 | B, 1-3 |  |  |  |  | Paint | Paint | Normal | - | - | - | - | - | Main Elec Rm - Basement | - | N/A | - | [5 empty] | N | [5 empty] | What does the group want to do here, and do we want to provide pre transfer signal? Need to run calcs on (30/40HP) May be able to add to an existing Lifesafety ATS.
General Research Building | Up to Contractor and material | N/A - Basement | 1 | Traction - Basement | 3000 | Passenger | ST 1364 | B, 1-3 |  |  |  |  | Paint | Paint | Normal | - | - | - | - | - | Main Elec Rm - Basement | - | N/A | - | [5 empty] | N
Health Science Research Facility I | Priority 2 | ELM 053 | 5 | Traction | 3500 | Passenger | ST 1597 | 1-5 |  |  |  |  | Stainless | Stainless | Normal | n/a | MCC61 | RM 664 | - | - | Penthouse | N | N/A | - | [5 empty] | N |  |  |  |  | May be able to keep this off emergency, but can we add this? | Wha does the group want to do here? Confirm with Tim if this car is required to be on E-power. Possibly able to move this from normal MCC to EMCC.
Health Science Research Facility I | Priority 2 | ELM 053 | 4 | Traction | 5000 | Passenger | ST 1596 | L, LD, 2-6, PH |  |  |  |  | Stainless | Stainless | Emergency (Simplex) | n/a | EMCCP1 | Penthouse | ATS 4 | 1000a | Penthouse - Big MCC | N | N/A | ASCO | [5 empty] | N | Key for PH | Floor Control | Cab COP | Cab COP |  | Scopes seems to replace in kind, agreed?
Health Science Research Facility I | Priority 2 | ELM 052 | 2 | Traction | 3500 | Passenger | ST 1592 | 1-6 |  |  |  |  | Stainless | Stainless | Normal | n | MCCP1 | Penthouse | - | - | Penthouse |  | N/A | - | [5 empty] | N |  |  |  |  | (2) emegency MCCs, and (1) normal MCC | Wha does the group want to do here? Disconnects to be changed over from normal feeder to emergency feeder via selector, only one car will run on e-power at a time. UMB to deceide the best way and provide direction.
Health Science Research Facility I | Priority 2 | ELM 052 | 3 | Traction | 3500 | Passenger | ST 1593 | 1-6 |  |  |  |  | Stainless | Stainless | Normal | n | MCCP1 | Penthouse | - | - | Penthouse |  | N/A | - | [5 empty] | N |  |  |  |  | (2) emegency MCCs, and (1) normal MCC
Health Science Research Facility I | Priority 2 | ELM 052 | 1 | Traction | 3500 | Passenger | ST1591 | 1-6 |  |  |  |  | Stainless | Stainless | Emergency | n | EMCCP2 | Penthouse | ATS 6 | 600A | Penthouse - Small MCC |  | N/A | ASCO | [5 empty] | N |  |  |  |  | (2) emegency MCCs, and (1) normal MCC | Scopes seems to replace in kind, agreed?
Howard Hall | Up to Contractor and material | ELM 051 | 4 | Traction | 8500 | Passenger | ST 2061 | B, 1-6 |  |  |  |  | Stainless | Stainless | Emergency (Simplex) | - | EMPR | Penthouse | ATS/Meck | 600A | Main Sub - Basement |  | N/A | Cumins (Open Transition) | [5 empty] | N | [5 empty] | Scopes seems to replace in kind, agreed? Scope to Provide contacts for transfer and Pretransfer
Institute of Virology | Priority 1 |  | 2 | Traction | 3500 | Passenger | ST 1946 | B, 1-6 |  |  |  |  | Paint | Paint | Emergency | Y | EPEL | Penthouse | ATS | 3000a | Generator room - Penthouse |  | N/A | ASCO |  | Unified Power/Cummins) |  |  |  | N | [5 empty] | Scopes seems to replace in kind, agreed?
Institute of Virology | Priority 1 |  | 1 | Traction | 3500 | Passenger | ST1945 | 1-6 |  |  |  |  | Paint | Paint | Emergency | Y | EPEL | Penthouse | ATS | 3000a | Generator room - Penthouse |  | N/A | ASCO | [5 empty] | N
Institute of Virology | Priority 1 |  | 3 | Traction | 5000 | Passenger | ST 1947 | 1-6, PH |  |  |  |  | Paint | Paint | Emergency (Simplex) | Y | EPEL | Penthouse | ATS | 3000a | Generator room - Penthouse |  | N/A | ASCO | [5 empty] | N | Key for PH | Floor Control | Cab COP | Hall Station
Institute of Virology | Priority 1 |  | SWL | Drum Machine |  | Passenger | ST2005 | B, 1 |  |  |  |  | Paint | Paint | Emergency | - | - | - | - | - | - |  | N/A | - | [5 empty] | N | [5 empty] | Does this follow the same code as the EMRs? If so, we will need cooling and emergency…Most likely. Do we want to do anything with the cover for the water? |  | Direct replacment, no additional needs here.
Maryland Bar | Up to Contractor and material |  | 1 | Hydraulic |  | Passenger | ST1442 | B,1-3 | [6 empty] | Normal (none available in building) | - | - | - | - | - | - |  | N/A | - | [5 empty] | N | [7 empty] | Tim to provide scope for battery back up.
***we are not intending on adding elevators to emergency power. What elevators are on emergency power and are they on a selector switch or are they all fed simultaneuously.
*Nice to have
**Moranto and Bethal - Only High voltage contractors